## Example
EVALUATION OF WATER PUMPING SYSTEMS
Calculation Sheet
NOTE 1: The cells in green will be calculated automatically, do not enter any information.
NOTE 2: The cells in yellow must be filled with the proper information according to the reference manual.
Energy Audit of Pumping System
|  | Site: | [11 empty] | Date:
UTILITY:
SYSTEM: | [10 empty] | EQUIPMENT:
1.1. ELECTRICAL SYSTEM
POWER SUPPLY:
|  | Supplier: |  | NEC BS
|  | Service No.: |  | D-3364605
|  | Contract Tariff: |  | 3
TRANSFORMER:
|  | Type: |  | Pole-mounted three phase
|  | Capacity: |  | 3 x 25 kVA | 25
|  | Rated Voltage: |  | 13,800 / 440 V |  | V
MAIN SWITCH
|  | Make: |  | Moeller electric
|  | Capacity: |  | 40A
|  | Setting: |  | 32-40A
STARTER:
|  | Type: |  | Stator Resistance Starter
|  | Capacity: |  | 40 HP |  | HP
PROTECTION
|  | Make: |  | MOELLER ELECTRIC
|  | Capacity: |  | 32-40A |  |  |  | CAPACITORS
|  | Setting: |  | 37 A | [5 empty] | Capacity: | -- | kVAr |  | CONDUCTORS
| GROUNDING SYSTEM | [13 empty] | Service Entrance - Starter
|  | Is there a grounding system? | [5 empty] | YES | NO | [6 empty] | Caliber: |  | 10 | mm2
|  | Separated neutral and ground? | [5 empty] | YES | NO | [6 empty] | Length: |  | 15 | m
|  | Grounded transformed? | [5 empty] | YES | NO |  | Caliber: |  |  |  |  | Grouping:
|  | Grounded starter? | [5 empty] | YES | NO |  | Caliber: | 6 |  |  | Starter - Motor
|  | Grounded motor? | [5 empty] | YES | NO |  | Caliber: |  |  |  |  | Caliber:
[18 empty] | 12 | AWG
| OBSERVATIONS: | [14 empty] | Length: |  | 53 | m
[16 empty] | Grouping: |  | 3W / Conduit
1.2 NOMINAL MOTOR DATA
Nameplate Data:
|  | Make: |  | GRUNDFOS |  |  |  |  | Voltage: |  | 440 |  | V |  |  | Type: | SUBMERSIBLE
|  | Capacity: |  | 10 |  | HP |  |  | Current: |  | 15 |  | A |  |  | Frame:
|  | Speed: |  | 3450 |  | RPM |  |  | Efficiency: |  | 79% |  |  |  |  | SF: | 0.85
HISTORY:
|  | Age: |  | 1 |  | years |  | # of rewindings: |  |  | 0 |  |  |  |  | Operation: | 8760 | hrs/year
| OBSERVATIONS: |  |  | The motor has been overloaded and stopped five times this year for a period of 2 hours
1.3 NOMINAL PUMP DATA
| FRAME | [8 empty] | IMPELLER
|  | Make: | GRUNDFOS | [7 empty] | Type: |  | closed
|  | Type: | SUBMERSIBLE | [7 empty] | Material: |  | SS
|  | Model: | Sp 45-4N | [7 empty] | Diameter: | [6 empty] | m
|  | Age: |  | 1 |  |  |  |  | years |  | Age: |  | 1 |  |  |  |  | years
| SHAFT: |  |  |  |  | Diameter: |  |  | inches |  | Length: | [6 empty] | m
| DESIGN DATA: |  |  |  |  | Design Head: |  | 22 | m |  | Design Flow: |  | 18.61 |  |  |  |  | l/s
| OBSERVATIONS: |  |  | The pump has been stopped for 24 hours. There are no records of the pump's age
1.4 FLUID CHARACTERISTICS
| Fluid: |  | water |  |  |  |  | Temperature: |  | 21 | °C | [5 empty] | Density: | 1000 | kg/m3
OBSERVATIONS:
2.1 HYDRAULIC MEASUREMENTS
LEVELS:
|  | Tank suction level (A): | [5 empty] | 32.42 | m | [6 empty] | Suction Pipe Length (B): | 39.95 | m
|  | Distance of Discharge Pressure Gauge (C) | [5 empty] | 0.28 | m | [6 empty] | Height of Gauge (D): | 0.98 | m
[5 empty] | Diameter (m) |  |  | Material |  |  | Pressure (kg/cm2) |  |  |  | Flow (l/s) |  |  | Speed (m/s)
| Suction |  |  |  | 0.1 |  |  | SS | [6 empty] | 4.7 |  |  | 0.59842
| Discharge |  |  |  | 0.1 |  |  | SS |  |  |  | 1.3 |  |  | 4.7 |  |  | 0.59842
| TOPOGRAPHY: |  |  | Elevation of the pump site: |  |  |  |  | 1045 | masl | (meters above sea level)
|  |  |  | Elevation of the highest delivery point: |  |  |  |  | 1047 | masl
| OBSERVATIONS: |  |  | The well is deviated, so the pump must be submersible.
2.2 ELECTRICAL MEASUREMENTS
| VOLTAGE IN PHASES: | [5 empty] | Van: | 260.4 |  |  | Vbn: | 261.9 |  |  |  |  | Vcn: | 255.8
| CURRENT PHASE: | [5 empty] | Ia: | 13.92 |  |  | Ib: | 14.14 |  |  |  |  | Ic: | 12.93
| ACTIVE POWER: | [5 empty] | Pa: | 2.92 |  |  | Pb: | 2.86 |  |  |  |  | Pc: | 2.61
| POWER FACTOR | [5 empty] | PFa: | 0.806 |  |  | PFb: | 0.774 |  |  |  |  | PFc: | 0.791
| HARMONIC DISTORTION: | [5 empty] | THD-V: |  |  |  | THD-I:
| MEASUREMENT POINT: |  |  |  | Main circuit
| CAPACITOR CHECK: | [5 empty] | Ia: |  |  |  | Ib: | [5 empty] | Ic:
| GROUND SYSTEM: |  |  |  | Continuity: |  |  | YES | NO | Current: |  |  |  | A |  | Resistance: |  |  | Ω
| OBSERVATONS: |  |  | Did not find continuity in the grounding wire, so no measurements were made of current and resistance
2.3 TEMPERATURE MEASUREMENTS
| Control Equipment |  |  | Switch Input |  |  | Output Switch |  |  |  |  | Starter Input |  |  |  |  | Starter Output
|  |  |  | A | B | C | A |  | B | C |  | A | B |  |  | C | A | B | C
|  |  |  | 40 | 41 | 39 | 53 |  | 49 | 40 |  | 46 | 44 |  |  | 52 | 43 | 42 | 54
| MOTOR |  |  |  | TRANSFORMERS
| Housing |  | Bearings |  | Feeder Terminals |  |  |  | Low Voltage Terminals | [6 empty] | Frame |  | Radiator
|  |  | Upper | Lower | X1 | X2 | X3 |  | X0 | X1 |  | X2 | X3 |  |  | Upper | Lower | Upper | Lower
| 42 |  | 48 | 40 | 38 | 39 | 39 |  | 36 | 40 |  | 38 | 39 |  |  | 41 | 40 | 41 | 39
OBSERVATIONS:
3.1 ELECTRICAL CONDUCTORS EVALUATION
| Electrical Line: Indicate the beginning and the end of the line being evaluated |  |  |  |  | Caliber | Length |  | Resistance |  |  |  | Current |  |  | Operat. | Losses
[7 empty] | m |  | Ω/km |  | Ω |  | A |  |  | h/year | kW | kWh/year
| Current status |  | Transformer-Starter |  |  | 8 AWG | 15 |  | 2.1 |  | 0.0315 |  | 13.6633 |  |  | 8760 | 0.017642 | 154.543
|  |  | Starter-Motor |  |  | 12 AWG | 53 |  | 5.32 |  | 0.28196 |  | 13.6633 |  |  | 8760 | 0.15791 | 1383.3313
3.2 MOTOR EVALUATION
|  |  |  | Average |  | Unbalance |  |  | Status |  |  | V/Vn |  |  | EFFICIENCY EVALUATION
| VOLTAGE (V) |  |  | 445.3706 |  | 0.8008% |  |  | minimum |  |  | 1.221% |  |  | LF-Load Factor: |  |  | 85.98%
| CURRENT (A) |  |  | 13.6633 |  | 5.367% |  |  | average | [5 empty] | η nominal: |  |  | 77.95%
| POWER (kW) |  |  | 8.2321 |  | 6.675% |  |  | high | [5 empty] | Decrease: |  |  | 0.03152%
| PF-Power Factor |  |  | 78.11% |  | 2.091% |  |  | low | [5 empty] | η real: |  |  | 77.92%
MOTOR EFFICIENCY EVALUATION
| Horse Power |  | Effic' | LF | Effic. Nom. | Effic. 75% |  | Effic. 100% |  | FA ant |  | FA rew |  |  | FA vv |  | FA dv
| 10 |  | 77.92% | 85.98% | 77.95% | 76.9% |  | 79.3% |  | 0% |  | 0% |  |  | -0.00024434 |  | 99.99%
3.3 PUMP EVALUATION
PUMPING LOAD
|  | Suction line losses: |  |  | 0.12875 |  | m |  |  |  | Discharge line losses: |  |  |  |  | 0.001112 |  |  | m
|  | Specific gravity of fluid: |  |  | 1000 |  | kg/m3 |  |  |  | Discharge line speed: |  |  |  |  | 0.59842 |  |  | m/s
|  | Net pumping load: |  |  | 46.9199 |  | mwc |  |  |  | Deviation from design: |  |  |  |  | 113.3%
FLOW
|  | Flow measured: |  |  | 0.0047 |  | m3/s |  |  |  | Deviation from the design: |  |  |  |  | -74.74%
MANOMETER POWER
|  | Design: |  |  | 4.0164 |  | kW |  |  |  | Measurements: | 2.1633 | kW |  |  |  | Deviation: | -46.14%
EFFICIENCY:
|  | Electromecanical efficiency: |  |  | 26.28% | [5 empty] | Pump efficiency: |  |  |  |  | 33.72%
Pipe losses
|  |  | Q | A | v | Visco |  | Reynolds |  | Rug. Abs. |  | Rug. Rel. |  |  | fr |  | Hfr
|  |  | m3/s | m2 | m/s | m2/s |  |  |  | mm | [6 empty] | mca
| Suction |  | 0.0047 | 0.007854 | 0.59842 | 9.8165e-07 |  | 60960.4667 |  | 0.046 |  | 0.00046 |  |  | 0.021759 |  | 0.12875
| Discharge |  | 0.0047 | 0.007854 | 0.59842 | 9.8165e-07 |  | 60960.4667 |  | 0.046 |  | 0.00046 |  |  | 0.021759 |  | 0.001112
3.4 ACTUAL ENERGY BALANCE
| Parameter |  |  | Unit |  | Amount
| Energy consumption |  |  | kWh/year |  | 73650.943
| Motor efficiency |  |  | % |  | 77.92%
| Pump efficiency |  |  | % |  | 33.72%
| Leakage losses |  |  | % |  | 40%
| Useful head |  |  | wcm |  | 35.4
| Electrical losses |  |  | kWh/year |  | 1537.8742
| Motor losses |  |  | kWh/year |  | 15920.4121
| Pump losses |  |  | kWh/year |  | 37241.849
| Suction & discharge pipe losses |  |  | kWh/year |  | 52.4521
| Network head losses |  |  | kWh/year |  | 4652.8425
| Leakage losses |  |  | kWh/year |  | 5698.2052
| Useful work |  |  | kWh/year |  | 8547.3078
3.5 COMMENTS AND SAVINGS OPPORTUNITIES
|  | a). | There are several anomalies in the ground system, so a full assessment of standards compliance is recommended.
|  | b). | The power factor is low (78%), so it is recommended to install capacitor banks to reduce losses in electrical conductors by joule effect.
|  | c). | The temperature at the input and output terminals of the main switch and starter are high (above 40 ° C); consider performing predictive and preventive maintenance to maintain the good operation of equipment.
|  | d). | The imbalance in the calculated power is high, which is an indication that the motor is working poorly.
|  | e). | The pump efficiency is very low (33.36%), so we recommend replacing it
4.1 SAVINGS PROPOSAL DESCRIPTION
|  | 1). | Replace the sumersible pump and motor for more efficient equipment. The proposed equipment needs to be submersible because of the deviated well.
|  | 2). | Install a capacitor bank.
4.2 EQUIPMENT SPECIFICATION
|  | Pump specification |  |  |  | Make: |  |  |  |  | Goulds
[6 empty] | Model: |  |  |  |  | 5 RWAHC (3 Stages)
[6 empty] | Pump efficiency : |  |  |  |  | 0.735
|  | Motor specification |  |  |  | Nominal power: |  |  |  |  | 5 | HP
[6 empty] | Nominal voltage: |  |  |  |  | 440 | V
[6 empty] | Efficiency at full load: |  |  |  |  | 76.8 | %
[6 empty] | Number of phases: |  |  |  |  | 2
[6 empty] | Angular velocity: |  |  |  |  | 3500 | rpm
[6 empty] | Electromechanical efficiency: |  |  |  |  | 54.56%
|  | Capacitor bank |  |  |  | Capacity: |  |  |  |  | 1.8753 | kVar
[6 empty] | Nominal voltage: |  |  |  |  | 440 | V
4.3 ACTION PLAN
|  | Actions |  |  | i. | Replace sumersible pump equipment ; create a new proposal
[5 empty] | ii. | Reuse the same electric conductor and control equipment
[5 empty] | iii. | Install check valve
[5 empty] | iv. | Install capacitors bank
5.1 ELECTRICAL CONDUCTORS EVALUATION
| Electrical line: Indicate the beginning and the end of the line being evaluated |  |  |  |  | Caliber | Length |  | Resistance |  |  |  | Current |  |  | Operat. | Losses
[7 empty] | m |  | Ω/km |  | Ω |  | A |  |  | h/year | kW | kWh/year
| Current status |  | Transformer-Starter |  |  | 8 AWG | 15 |  | 2.1 |  | 0.0315 |  | 5.4103 |  |  | 8760 | 0.0027661 | 24.231
|  |  | Starter-Motor |  |  | 12 AWG | 53 |  | 5.32 |  | 0.28196 |  | 6.5657 |  |  | 8760 | 0.036464 | 319.4281
5.2 MOTOR EFFICIENCY CALCULATION
|  |  | PF | BHP | P propsed |  | Erfic. Real |  | LF |  | Effic. Nom. |  | Effic. 75% |  |  | Effic 100%
|  |  | 78.28% | 3.9455 | 5 |  | 74.24% |  | 78.91% |  | 74.27% |  | 73.8% |  |  | 76.8%
[11 empty] | FA ant |  | FA rew |  |  | FA vv |  | FA dv
[11 empty] | 0% |  | 0% |  |  | -0.00024434 |  | 99.99%
5.3 EXPECTED ENERGY BALANCE
| Parameter |  |  | Unit |  | Amount
| Energy consumption |  |  | kWh/year |  | 35074.4467
| Power demand |  |  | kW |  | 3.9647
| Current |  |  | A |  | 6.5657
| Power factor |  |  | % |  | 78.28%
| Electrical losses |  |  | kWh/year |  | 343.6591
| Motor losses |  |  | kWh/year |  | 8947.3758
| Pump losses |  |  | kWh/year |  | 6832.6041
| Suction pipe losses |  |  | kWh/year |  | 52.4521
| Network head losses |  |  | kWh/year |  | 4652.8425
| Leakage losses |  |  | kWh/year |  | 5698.2052
| Useful work |  |  | kWh/year |  | 8547.3078
| Savings |  |  | kWh/year |  | 38576.4963
6.1 CALCULATION OF SAVINGS
|  | Energy cost | [13 empty] | 0.12 |  | USD/kWh
|  | Direct savings |  |  |  | The direct benefits come from the reduction of losses in the pump and motor
[7 empty] | Energy Saved | [8 empty] | 38576.4963 |  | kWh/year
[7 empty] | Electricity Savings invoice | [8 empty] | 4629.1796 |  | USD/year
|  | Additional savings: |  |  |  | The proposed motor will work with a better power factor and will demand a lower current, which results in a reduced joule effect on conductors.
[7 empty] | Savings: energy conductors | [8 empty] | 1194.2151 |  | kWh/year
[7 empty] | Savings: electricity invoice | [8 empty] | 143.3058 |  | USD/year
6.2 INVESTMENT CALCULATION
|  | Item | Description | [9 empty] | Amount |  |  | Unit price (USD) |  | Total cost (USD)
|  | 1 | Submersible pump motor assembly | [9 empty] | 1 |  |  | 3431 |  | 3431
|  | 2 | Remove current pumping equipment and install proposed | [9 empty] | 1 |  |  | 1000 |  | 1000
|  | 3 | Capacitors Bank 5 kVar, 480 Volts. Supply and installation | [9 empty] | 1 |  |  | 245 |  | 245
|  | TOTAL: | [15 empty] | 5377.4
6.3 PROFITABILITY ANALYSIS
|  |  | Total savings: |  |  | Reduction of Energy Consumption (kWh/year): | [11 empty] | 38576.4963
[6 empty] | Savings (USD/year): |  | Total: | [9 empty] | 4629.1796
|  |  | Total investment: | [12 empty] | USD: |  | 5377.4
|  |  | Pay-back period: | [13 empty] | years: | 1.1616
Moeller electric
Motor -protective circuit-breaker (PKZ) 40 A
Moeller electric 40 HP
LLPP14
Service Entrance
Stator resistance starter
Dynamic level
Pressure gauge
Note: This spreadsheet has been filled in with an Example Data which must be replaced by the specific information of the pumping system the user wants to analyze. We recommend to save the file under the name of the corresponding pumping system before you start to fill it in. YELLOW FIELDS NEED TO BE REPLACED OR FILLED IN; GREEN FIELDS WILL BE CALCULATED AUTOMATICALLY.

## Steps
1 | DATA COLLECTION
| 1.1 | Electrical System
| 1.2 | Nominal Motor Data
| 1.3 | Nominal Pump Data
| 1.4 | Fluid Characteristics
2 | MEASUREMENTS
| 2.1 | Hydraulic Measurements
| 2.2 | Electrical Measurements
| 2.3 | Temperature Measurements
3 | EVALUATION
| 3.1 | Electrical Conductors Evaluation
| 3.2 | Motor Evaluation
| 3.3 | Pump Evaluation
| 3.4 | Actual Energy Balance
| 3.5 | Comments and Savings Opportunities
4 | SAVINGS PROJECT
| 4.1 | Savings Proposal Description
| 4.2 | Equipment Specification
| 4.3 | Action Plan
5 | SAVINGS EVALUATION
| 5.1 | Electrical Conductors Evaluation
| 5.2 | Motor Efficiency Calculation
| 5.3 | Expected Energy Balance
6 | ECONOMIC ANALYSIS
| 6.1 | Calculation of Savings
| 6.2 | Investment Calculation
| 6.3 | Profitability Analysis